- SSBF-47*– Barrier Free, recessed, wall mounted combination eye/face wash and horizontally mounted shower with patented stainless steel shower-actuating arm and swing-down stainless steel combination eye/face wash drain pan.  Unit shall be all welded 18-gauge type 304 stainless steel construction, with a stainless steel shower head, supply nipple, and escutcheon, chrome plated brass eye/face wash supply fittings, U.S. made brass unions, U.S made full-port brass ball valve for shower, eye/face wash valve shall be “Auto Flow”, plug-type design with Teflon coated “O” rings to seal valve orifices, polypropylene ‘FS Plus’ spray heads with individual 3.2-GPM flow controls and polyurethane filters. Supplied with in-line strainer to prevent debris from affecting the eye/face wash valve and 2” IPS drain. Activate eye wash valve by rotating 90° from stored position.  Unit shall include ANSI compliant sign.

- Performance: Unit complies with ADA requirements for accessibility by handicapped persons. Unit shall be fully factory assembled and hydrostatically tested to meet or exceed ANSI Z358.1 – 2004, and come with a full 2-year warranty.

- Fixture: Guardian GBF2170