- TMV -1 – Thermostatic mixing valve (factory set to 85 degrees) for single emergency eye wash.  Unit shall include a built-in cold water by-pass, rough bronze finish, solid bimetal thermostat, locking temperature regulator with limit stop factory set for 90 degrees, integral check stops, and dial thermometer.

- Performance:  Unit shall have a flow range of 0.5-GPM to 5-GPM with a maximum pressure loss of 20-PSI and come with a full 1-year warranty.

- Fixture:  Guardian G3600